## Engr.Walid Master bedroom
INPUT VALUES ARE TO BE GIVEN IN BLUE COLOR BOXES ONLY
PROJECT | [9 empty] | FLOOR | Ground Floor
LOCATION | U.A.E (ABU DHABI) | [8 empty] | SPACE REFERENCE | R-01, Flat-1, Bedroom,Residential (ABU DHABI)
CLIENT | XYZ | [8 empty] | AREA ( SqFt) (WxH) | 300
CONSULTANT | ABC | [8 empty] | Falce Ceiling Height (Ft) | 9.4
126 | [9 empty] | Volume (CuFt) | 2820
Item | Area or Quantity |  |  | Sun Gain or Temp. Diff. |  |  | Factor (U) | Btu/Hour | Watts | Estimate for | Summer
[10 empty] | Design Conditions | DB (°F) |  | WB (°F) | RH (%) | HR (Gr/Lb)
|  | ROOM HEAT |  |  | Q= U*A*ΔT |  |  |  |  | Ambient(Out Side) | 111 |  | 75 | 19 | 74
ROOM SENSIBLE HEAT | [9 empty] | Room (InDoor) | 75 |  | 63 | 50 | 68
Solar Gain - Glass | Area |  |  | ΔT |  |  | U |  |  | Difference Δ | 36 |  | 12 | -31 | 6
Glass - N |  | SqFt | x |  |  | x |  | 0
Glass - NE |  | SqFt | x |  |  | x |  | 0
Glass - E |  | SqFt | x |  |  | x |  | 0 |  | By Pass Factor (BF) |  |  |  |  | = | 0.12
Glass - SE | 15.5 | SqFt | x | 13 |  | x | 0.3 | 60.45 |  | Contact Factor (CF = 1 - BF) |  |  |  |  | = | 0.88
Glass - S |  | SqFt | x |  |  | x |  | 0 |  | CFM Ventilation
Glass - SW | 11.62 | SqFt | x | 100 |  | x | 0.3 | 348.6 |  | CFM Per Person | 5 | No | = | 2 | = | 10
Glass - W |  | SqFt | x |  |  | x |  | 0 |  | CFM Per SqFt | 0.06 | Sqft | x | 300 | = | 18
Glass - NW |  | SqFt | x |  |  | x |  | 0 |  | Air Change Per Hour (CFM) |  |  | =
Skylight |  | SqFt | x |  |  | x |  | 0 |  | CFM Cu.ft | 2820 | x | 0 | x1/60 | = | 0
Solar & Transmission Gain - Walls & Roof | [9 empty] | CFM Infiltration
Wall - N |  | SqFt | x |  | F | x |  | 0 |  | Swinging |  | x |  | cfm/door | = | 0
Wall - NE |  | SqFt | x |  | F | x |  | 0 |  | Revolving Doors (People) |  | x |  | cfm/door | = | 0
Wall - E |  | SqFt | x |  | F | x |  | 0 |  | Open Doors |  | x | 1 | cfm/door | = | 0
Wall - SE | 138.33 | SqFt | x | 37.5 | F | x | 0.05 | 259.3688 |  | Crack (feet) |  | x |  | cfm/ft | = | 0
Wall - S |  | SqFt | x |  | F | x |  | 0 | [7 empty] | 0
Wall - SW | 128.35 | SqFt | x | 35.5 | F | x | 0.05 | 227.8213 |  | Supply CFM from Machine
Wall - W |  | SqFt | x |  | F | x |  | 0 |  | Effective Room Sensible Heat Factor =
Wall - NW |  | SqFt | x |  | F | x |  | 0 |  | Effective Room Sensible Heat/Eff Room Total Heat |  |  |  |  | = | 0.96935
Roof | 300 | SqFt | x | 45.5 | F | x | 0.045 | 614.25 |  | Apparatus Dew Point (ADP)
Transmission Gain - Except Walls & Roof | [9 empty] | Indicated ADP (°F) |  |  |  |  | =
All Glass | 27.1 | SqFt | x | 36 | F | x | 0.3 | 292.68 |  | Selected ADP (°F) |  |  |  |  | = | 54.6
Partition | 46.15 | SqFt | x | 31 | F | x | 0.5 | 715.325 |  | Dehumidified Rise
Ceiling |  | SqFt | x |  | F | x |  | 0 |  | (Room DB - ADP) x CF |  |  |  |  | = | 17.952
Floor | 300 | SqFt | x | 31 | F | x | 0.27 | 2511 |  | DEHUMIDIFIED AIR QUANTITY
INFILTRATION AND BY PASSED AIR | [9 empty] | Effective Room Sensible Heat |  |  | = | 434.4869 |  | CFM
Infiltration |  | CFM | x | 36 | T.Diff | x | 1.08 | 0 |  | Dehumidified Rise x 1.08
Outside Air | 28 | CFM | x | 36 |  | x |  | 130.6368
Internal Heat | [12 empty] | = | 204.2088 |  | L/s
People | 2 | Nos. | x | 230 | Btu/Hour Per Person |  |  | 460 |  | TOTAL HEAT CAPACITY
Lighting | 300 | SqFt | x | 1 | W/SqFt | x | 3.41 | 1023 |  | Grand Total Heat |  |  | = | 0.83677 |  | TR
Equipments | 1 |  |  | 200 | Watts | x | 3.41 | 682
Power |  | kW/Hp | x |  |  |  |  | 0
Sub Total | [7 empty] | 7325.1318
Factor | [6 empty] | 5-15% | 1098.7698
Effective Room Sensible Heat | [7 empty] | 8423.9016 | 1 | SENSIBLE HEAT CAPACITY
ROOM LATENT HEAT | [9 empty] | Grand Sensible Heat |  |  | = | 0.83677 |  | TR
Infiltration | 0 | CFM | x | 6 | Gr/Lb | x | 0.68 | 0 |  | 12000
Outside Air | 28 | CFM | x | 6 | Gr/Lb | x | BFx0.68 | 13.7088
People | 2 | Nos. | x | 120 | Btu/Hour Per Person |  |  | 240
Sub Total | [7 empty] | 253.7088
Factor | [6 empty] | 2.5 - 5% | 12.6854
Effective Room Latent Heat | [7 empty] | 266.3942 | 2
EFFECTIVE ROOM TOTAL HEAT | [7 empty] | 8690.2958
OUTSIDE AIR HEAT
Sensible | 28 | CFM | x | 36 | F(TD) | x | CF x 1.08 | 958.0032 | 3
Latent | 28 | CFM | x | 6 | Gr/Lb | x | CF x 0.68 | 100.5312 | 4
OUTSIDE AIR TOTAL HEAT | [7 empty] | 1058.5344 |  | Notes:
GRAND SUB-TOTAL HEAT | [7 empty] | 9748.8302
Factor | [6 empty] | 1 - 3% | 292.4649
GRAND TOTAL HEAT | [7 empty] | 10041.2951
[7 empty] | TMBH | 10.0413
[7 empty] | TKW | 2.912
[7 empty] | TSMBH | 9381.9048
[7 empty] | TSKW | 2720.7524
TONS=GRAND TOTAL HEAT/12000 | [7 empty] | 0.83677
Note on L6: False Ceiling Height
Note on Q15: Select From Data Book
Note on L18: CFM/Person
Note on O18: No of People
Note on L19: CFM/SQFT Area
Note on O20: Genarally NACPH for Residentia l-->1 to 3 NACPH for Commercial-->2 to 3 NACPH for Industrial -->2 to 5
Note on B34: Area For Non air Conditioned to Air Conditioned Partition Area only
Note on E42: 1 watt / Sqft For Residential 1.25 to 1.5 watt / Sqft For Commertial 1.5 to 2.0 watt / Sqft For Industrial
Note on H42: 1 Watt = 3.415 Btu /Hr
Note on E43: Data can be aquired from Client.
Note on H43: 1 Watt = 3.415 Btu /Hr
Note on B49: infilteration Can Be 2 to 5 CFM
Note on B50: Taken Max of W.R.T People, Area, NACPH
Note on B57: Taken Max of W.R.T People, Area, NACPH
Note on B58: Taken Max of W.R.T People, Area, NACPH

## Master Bedroom Example
INPUT VALUES ARE TO BE GIVEN IN BLUE COLOR BOXES ONLY
PROJECT | [9 empty] | FLOOR | Ground Floor
LOCATION | U.A.E (DUBAI) | [8 empty] | SPACE REFERENCE | R-01, Flat-1, Master Bedroom,Residential (DUBAI)
CLIENT | XYZ | [8 empty] | AREA ( SqFt) (WxH) | 360
CONSULTANT | ABC | [8 empty] | Falce Ceiling Height (Ft) | 12.5
126 | [9 empty] | Volume (CuFt) | 4500
Item | Area or Quantity |  |  | Sun Gain or Temp. Diff. |  |  | Factor (U) | Btu/Hour | Watts | Estimate for | Summer
[10 empty] | Design Conditions | DB (°F) |  | WB (°F) | RH (%) | HR (Gr/Lb)
|  | ROOM HEAT |  |  | Q= U*A*ΔT |  |  |  |  | Ambient(Out Side) | 107 |  | 75 | 24 | 80
ROOM SENSIBLE HEAT | [9 empty] | Room (InDoor) | 75 |  | 63 | 50 | 68
Solar Gain - Glass | Area |  |  | ΔT |  |  | U |  |  | Difference Δ | 32 |  | 12 | -26 | 12
Glass - N | 15 | SqFt | x | 13 |  | x | 0.3 | 58.5
Glass - NE |  | SqFt | x |  |  | x |  | 0
Glass - E |  | SqFt | x |  |  | x |  | 0 |  | By Pass Factor (BF) |  |  |  |  | = | 0.12
Glass - SE |  | SqFt | x |  |  | x |  | 0 |  | Contact Factor (CF = 1 - BF) |  |  |  |  | = | 0.88
Glass - S |  | SqFt | x |  |  | x |  | 0 |  | CFM Ventilation
Glass - SW |  | SqFt | x |  |  | x |  | 0 |  | CFM Per Person | 5 | No | = | 2 | = | 10
Glass - W | 15 | SqFt | x | 145 |  | x | 0.3 | 652.5 |  | CFM Per SqFt | 0.06 | Sqft | x | 360 | = | 21.6
Glass - NW |  | SqFt | x |  |  | x |  | 0 |  | Air Change Per Hour (CFM) |  |  | =
Skylight |  | SqFt | x |  |  | x |  | 0 |  | CFM Cu.ft | 4500 | x | 0 | x1/60 | = | 0
Solar & Transmission Gain - Walls & Roof | [9 empty] | CFM Infiltration
Wall - N | 225 | SqFt | x | 26.5 | F | x | 0.05 | 298.125 |  | Swinging |  | x |  | cfm/door | = | 0
Wall - NE |  | SqFt | x |  | F | x |  | 0 |  | Revolving Doors (People) |  | x |  | cfm/door | = | 0
Wall - E |  | SqFt | x |  | F | x |  | 0 |  | Open Doors |  | x | 1 | cfm/door | = | 0
Wall - SE |  | SqFt | x |  | F | x |  | 0 |  | Crack (feet) |  | x |  | cfm/ft | = | 0
Wall - S |  | SqFt | x |  | F | x |  | 0 | [7 empty] | 0
Wall - SW |  | SqFt | x |  | F | x |  | 0 |  | Supply CFM from Machine
Wall - W | 250 | SqFt | x | 35.5 | F | x | 0.05 | 443.75 |  | Effective Room Sensible Heat Factor =
Wall - NW |  | SqFt | x |  | F | x |  | 0 |  | Effective Room Sensible Heat/Eff Room Total Heat |  |  |  |  | = | 0.97012
Roof | 360 | SqFt | x | 49 | F | x | 0.045 | 793.8 |  | Apparatus Dew Point (ADP)
Transmission Gain - Except Walls & Roof | [9 empty] | Indicated ADP (°F) |  |  |  |  | =
All Glass | 30 | SqFt | x | 32 | F | x | 0.3 | 288 |  | Selected ADP (°F) |  |  |  |  | = | 54.7
Partition | 150 | SqFt | x | 27 | F | x | 0.5 | 2025 |  | Dehumidified Rise
Ceiling |  | SqFt | x |  | F | x |  | 0 |  | (Room DB - ADP) x CF |  |  |  |  | = | 17.864
Floor | 360 | SqFt | x | 27 | F | x | 0.1 | 972 |  | DEHUMIDIFIED AIR QUANTITY
INFILTRATION AND BY PASSED AIR | [9 empty] | Effective Room Sensible Heat |  |  | = | 478.7808 |  | CFM
Infiltration |  | CFM | x | 32 | T.Diff | x | 1.08 | 0 |  | Dehumidified Rise x 1.08
Outside Air | 31.6 | CFM | x | 32 |  | x |  | 131.0515
Internal Heat | [12 empty] | = | 225.027 |  | L/s
People | 2 | Nos. | x | 230 | Btu/Hour Per Person |  |  | 460 |  | TOTAL HEAT CAPACITY
Lighting | 360 | SqFt | x | 1 | W/SqFt | x | 3.41 | 1227.6 |  | Grand Total Heat |  |  | = | 0.91924 |  | TR
Equipments | 1 |  |  | 200 | Watts | x | 3.41 | 682
Power |  | kW/Hp | x |  |  |  |  | 0
Sub Total | [7 empty] | 8032.3265
Factor | [6 empty] | 5-15% | 1204.849
Effective Room Sensible Heat | [7 empty] | 9237.1755 | 1 | SENSIBLE HEAT CAPACITY
ROOM LATENT HEAT | [9 empty] | Grand Sensible Heat |  |  | = | 0.91924 |  | TR
Infiltration | 0 | CFM | x | 12 | Gr/Lb | x | 0.68 | 0 |  | 12000
Outside Air | 31.6 | CFM | x | 12 | Gr/Lb | x | BFx0.68 | 30.9427
People | 2 | Nos. | x | 120 | Btu/Hour Per Person |  |  | 240
Sub Total | [7 empty] | 270.9427
Factor | [6 empty] | 2.5 - 5% | 13.5471
Effective Room Latent Heat | [7 empty] | 284.4899 | 2
EFFECTIVE ROOM TOTAL HEAT | [7 empty] | 9521.6654
OUTSIDE AIR HEAT
Sensible | 31.6 | CFM | x | 32 | F(TD) | x | CF x 1.08 | 961.0445 | 3
Latent | 31.6 | CFM | x | 12 | Gr/Lb | x | CF x 0.68 | 226.9133 | 4
OUTSIDE AIR TOTAL HEAT | [7 empty] | 1187.9578 |  | Notes:
GRAND SUB-TOTAL HEAT | [7 empty] | 10709.6231
Factor | [6 empty] | 1 - 3% | 321.2887
GRAND TOTAL HEAT | [7 empty] | 11030.9118
[7 empty] | TMBH | 11.0309
[7 empty] | TKW | 3.199
[7 empty] | TSMBH | 10198.22
[7 empty] | TSKW | 2957.4838
TONS=GRAND TOTAL HEAT/12000 | [7 empty] | 0.91924
Note on L6: False Ceiling Height
Note on Q15: Select From Data Book
Note on L18: CFM/Person
Note on O18: No of People
Note on L19: CFM/SQFT Area
Note on O20: Genarally NACPH for Residentia l-->1 to 3 NACPH for Commercial-->2 to 3 NACPH for Industrial -->2 to 5
Note on B34: Area For Non air Conditioned to Air Conditioned Partition Area only
Note on E42: 1 watt / Sqft For Residential 1.25 to 1.5 watt / Sqft For Commertial 1.5 to 2.0 watt / Sqft For Industrial
Note on H42: 1 Watt = 3.415 Btu /Hr
Note on E43: Data can be aquired from Client.
Note on H43: 1 Watt = 3.415 Btu /Hr
Note on B49: infilteration Can Be 2 to 5 CFM
Note on B50: Taken Max of W.R.T People, Area, NACPH
Note on B57: Taken Max of W.R.T People, Area, NACPH
Note on B58: Taken Max of W.R.T People, Area, NACPH